## cover
PNM 2017 IRP
New and Existing Resource Data Assumptions
Working Document dated 11-10-2016

## New Conventional
|  |  |  | New Resource Alternatives Performance Data - Conventional Resources | [6 empty] | New Resource Alternatives Performance Data - Conventional Resources
|  |  |  | Small | Large | Mid | Large | Reciprocating | Combined | Rio | Combined | Palo Verde | Palo Verde | Battery | Battery
|  |  |  | Aeroderivative | Aeroderivative | Gas Turbine | Gas Turbine | Engines | Cycle | Bravo | Cycle | Unit 1 | Unit 2 | 2 hr | 4 hr
Line | [8 empty] | New Build | Expansion | Existing | Ownership | Ownership | Storage | Storage
1 | Expected Facility Output |  | MW | 40 | 85 | 140 | 187 | 82 | 289 | 210 | 250 | 104 | 10 | 2 | 40
2 |  | (@ 4000 ft, 90 F)
3 | Estimated ELCC |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
4 |  | Tier 2 - 80 MW
5 |  | Tier 3 - 120 MW
6 |  | Tier 4 - >80 MW
7
8 | Estimated Heatrate @ max output |  | Btu/kWh | 9800 | 9800 | 10400 | 9600 | 8800 | 6998.58 | 7200 | 7000 | 10300 | 10300 | Charging tech | Charging tech
9
10 | Expected Capacity Factor |  | % | 5-15% | 5-15% | 5-25% | 5-25% | 5-65% | 25-65% | 25-65% | 25-65% | 0-100% | 0-100% | 0-15% | 0-15%
11
12 | Forced Outage Rate |  | % | 3% | 3% | 3% | 3% | 3% | 5% | 5% | 5% | 2% | 2% | 2% | 2%
13
14 | Emission Rates
15 |  | CO2 Rate | lbs/MWh | 1140 | 1115 | 1300 | 1300 | 980 | 845 | 845 | 845 | 0 | 0 | 0 | 0
16 |  | CO Rate | lbs/MWh | 0.08918 | 0.28 | 0.18 | 0.18 | 0.26 | 0.12 | 0.12 | 0.12 | 0 | 0 | 0 | 0
17 |  | SO2 Rate | lbs/MWh | 0.13132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 |  | NOx Rate | lbs/MWh | 0.0098 | 0.11 | 0.39 | 0.39 | 3.65 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0 | 0
19 |  | Hg Rage | lbs/MWh | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 |  | PM10 Rate | lbs/MWh | 0.083779 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0
21 |  | Water Usage | gal/MWh | 100 | 150 | 50 | 50 | 150 | 150 | 150 | 600 | 18.1702 | 18.1702 | 0 | 0
22
23 | Construction Time |  | months | 9 | 12 | 12 | 12 | 12 | 24 | 24 | 24 |  |  | 24 | 24
24
25 | First Year Available |  | Year | 2020 | 2020 | 2020 | 2020 | 2020 | 2021 | 2022 | 2021 | 2024 | 2023 | 2021 | 2021
26
27 | Facility Life |  | Years | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 29 | 29 | 30 | 30
28
29
30 |  |  |  | New Resource Alternatives Cost & Financial Data - Conventional Resources | [6 empty] | New Resource Alternatives Cost & Financial Data - Conventional Resources
31 |  |  |  | Small | Large | Mid | Large | Reciprocating | Combined | Rio | Combined | Palo Verde | Palo Verde | Battery | Battery
32 |  |  |  | Aeroderivative | Aeroderivative | Gas Turbine | Gas Turbine | Engines | Cycle | Bravo | Cycle | Unit 1 | Unit 2 | 2 hr | 4 hr
33 | [8 empty] | New Build | Expansion | Existing | Ownership | Ownership | Storage | Storage
34 | Expected Facility Output |  | MW | 40 | 85 | 140 | 187 | 82 | 289 | 210 | 250 | 104 | 10 | 2 | 40
35 |  | (@ 4000 ft, 90 F)
36 | Investment Tax Credit - Federal |  | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37
38 | Production Tax Credit - Federal |  |  | No | No | No | No | No | No | No | No | No | No | No | No
39
40 | Production Tax Credit - State |  |  | No | No | No | No | No | No | No | No | No | No | No | No
41
42 | Proxy Property Tax |  | % | 2.7% | 2.7% | 2.7% | 2.7% | 2.7% | 2.7% | 2.7% | 1.25% | 1.25% | 1.25% | 2.7% | 2.7%
43
44 | Utility Ownership
45
46 | Capital Cost
47 |  | Construction Cost |  | 38000 | 78000 | 116000 | 126000 | 87000 | 258000 | 145200 | 0 | 0 | 0 | 0 | 0
48 |  | Transmission/Other Costs |  | 3000 | 5000 | 5000 | 5000 | 5000 | 10000 | 5000 | 0 | 0 | 0 | 0 | 0
49 |  | AFUDC |  | 1600 | 3200 | 6400 | 10500 | 5000 | 20000 | 10800 | 0 | 0 | 0 | 0 | 0
50 |  | Owners Costs |  | 3500 | 4500 | 5400 | 5000 | 4500 | 10200 | 7500 | 0 | 0 | 0 | 0 | 0
51 | Total Capital Costs |  | k$ | 46100 | 90700 | 132800 | 146500 | 101500 | 298200 | 168500 | 175000 | 260000 | 25000 | 3700 | 114400
52
53 | Total Capital Costs |  | $/kW | 1152.5 | 1067.0588 | 948.5714 | 783.4225 | 1237.8049 | 1031.8339 | 802.381 | 700 | 2500 | 2500 | 1850 | 2860
54
55 | Revenue Requirements (Capital Only) |  | k$ | 88487.7155 | 122366.3877 | 179004.5014 | 197149.3106 | 136804.2911 | 401424.8203 | 227183.483 | 236675.8833 | 253837.2834 | 23812.1279 | 147878.2362 | 99313.025
56
57 | Cost of Capital |  | % | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71%
58
59 | Reference Year Dollars |  |  | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2024 | 2023 | 2017 | 2017
60
61 | Fixed O&M |  | $/kWyr
62 |  | Base O&M |  | 7.43 | 5.99 | 15 | 22.19 | 24.9351 | 27.33 | 27.4708 | 22 | 151.2025 | 168.6983 | 28 | 39
63 |  | Gas Reservation |  | 26 | 26 | 26 | 26 | 26 | 26 | 18.1 | 26 | 0 | 0 | 0 | 0
64 |  | Transmission Service |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.8493 | 39.57 | 39.57 | 0 | 0
65 |  | Property Taxes |  | 10.3725 | 9.6035 | 8.5371 | 7.0508 | 11.1402 | 9.2865 | 8.2177 | 8.75 | 13.7892 | 13.7892 | 16.65 | 25.74
66 |  | Total |  | 43.8025 | 41.5935 | 49.5371 | 55.2408 | 62.0754 | 62.6165 | 53.7885 | 97.5993 | 204.5616 | 222.0574 | 44.65 | 64.74
67
68 | Variable O&M
69 |  | Base O&M |  | 5.26 | 4.64 | 4 | 2.56 | 2.2076 | 2.55 | 0 | 0 | 0 | 0 | Charging Tech | Charging Tech
70 |  | Integration Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | Total Variable O&M costs |  | $/mwh | 5.26 | 4.64 | 4 | 2.56 | 2.2076 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0
72
73 | PPA
74
75 | Energy Price
76 |  | Base Energy Price | $/mwh
77 |  | Transmission Upgrades/ | $/mwh
78 |  | Interconnection | $/mwh
79 |  | PPA Administration | $/mwh
80 |  | Integration Costs | $/mwh
81 | Total Energy Price |  | $/mwh
82
83 | Reference Year Dollars
84
85 | Annual Escalation |  | %
86
87 |  |  |  | Data on this table represents planning assumptions as of 11/09/16. | [6 empty] | Data on this table represents planning assumptions as of 11/09/16.
88 |  |  |  | represents a sensitivity will be performed | [6 empty] | represents a sensitivity will be performed

## New Renewables
New Resource Alternatives Performance Data - Renewable Resources
|  |  |  | Solar | Solar | Solar | Solar | Solar | Wind | Wind | Geothermal
|  |  |  | Photovoltaic | Photovoltaic | Photovoltaic | Power Tower | Photovoltaic
Line |  |  |  | Tracking | Tracking | Tracking | 10 hr storage | Tracking
1 | Nameplate Facility Output |  | MW | 10 | 49.5 | 99 | 100 | 49.5 | 50 | 100 | 15
2
3 | Estimated ELCC |  | % | [5 empty] | 5% | 5% | 100%
4 |  | Tier 2 - 80 MW | % | 71% | 71% | 71% | 100% | 71%
5 |  | Tier 3 - 140 MW | % | 52% | 52% | 52% | 100% | 52%
6 |  | Tier 4 - >80 MW | % | 19.5% | 19.5% | 19.5% | 100% | 19.5%
7
8 | Estimated Heatrate @ max output |  | Btu/kWh
9
10 | Expected Capacity Factor |  | % | 33% | 33% | 33% | 45% | 33% | 40% | 40% | 85%
11
12 | Forced Outage Rate |  | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
13
14 | Emission Rates
15 |  | CO2 Rate | lbs/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 |  | CO Rate | lbs/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 |  | SO2 Rate | lbs/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 |  | NOx Rate | lbs/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 |  | Hg Rage | lbs/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 |  | PM10 Rate | lbs/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 |  | Water Usage | gal/MWh | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 100
22
23 | Construction Time |  | months | 9 | 15 | 15 | 24 | 15 | 24 | 24 | 24
24
25 | First Year Available |  | Year | 2018 | 2019 | 2019 | 2020 | 2019 | 2018 | 2018 | 2021
26
27 | Facility Life |  | Years | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 30
28
29
30 |  |  |  | New Resource Alternatives Cost & Financial Data - Renewable Resources
31 |  |  |  | Solar | Solar | Solar | Solar | Solar | Wind | Wind | Geothermal
32 |  |  |  | Photovoltaic | Photovoltaic | Photovoltaic | Power Tower | Photovoltaic
33 |  |  |  | Tracking | Tracking | Tracking | 10 hr storage | Tracking
34 | Nameplate Facility Output |  | MW | 10 | 49.5 | 99 | 100 | 49.5 | 50 | 100 | 15
35
36 | Investment Tax Credit - Federal* |  | % | Yes | Yes | Yes | Yes | Yes | 0 | 0 | 10%
37
38 | Production Tax Credit - Federal | [7 empty] | Yes | Yes | Yes
39
40 | Production Tax Credit - State |  |  | No | No | No | No | No | No | No | No
41
42 | Proxy Property Tax |  | % | 2.64% | 2.64% | 2.64% | 2.64% | 2.64% | 2.64% | 2.64% | 2.64% | *Tax Credits
43 | [12 empty] | Federal | Federal
44 | Utility Ownership | [11 empty] | ITC | PTC
45 | [11 empty] | Solar Inservice < 2020 | 30%
46 | Capital Cost | [10 empty] | Solar Inservice 2020 | 26%
47 |  | Construction Cost |  | 14575.6098 | 79365.5345 | 158731.0689 | [5 empty] | Solar Inservice 2021 | 22%
48 |  | Transmission/Other Costs |  | 1365.8537 | 8626.6885 | 17253.3771 | [5 empty] | Solar Inservice > 2021 | 10%
49 |  | AFUDC |  | 178.5564 | 943.9192 | 1887.8385 | [5 empty] | Geothermal | 10%
50 |  | Owners Costs |  | 585.3659 | 4313.3443 | 8626.6885 | [5 empty] | Wind Construction 2017 |  | 1.93 cents
51 | Total Capital Costs |  | k$ | 16705.3856 | 93249.4865 | 186498.973 | [5 empty] | Wind Construction 2018 |  | 1.49 cents
52 | [11 empty] | Wind Construction 2019 |  | 1.02 cents
53 | Total Capital Costs |  | $/kW | 1670.5386 | 1883.828 | 1883.828
54
55 | Revenue Requirements (Capital Only) |  | k$ | 19214.491 | 103082.166 | 206164.3321
56
57 | Cost of Capital |  | % | 7.71% | 7.71% | 7.71%
58
59 | Reference Year Dollars |  | Yr | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017
60
61 | Fixed O&M |  | $/kWyr
62 |  | Base O&M |  | 27.87 | 20.95 | 20.95
63 |  | Property Taxes |  | 14.7007 | 16.5777 | 16.5777
64 |  | Total |  | 42.5707 | 37.5277 | 37.5277
65
66 | Variable O&M
67 |  | Base O&M |  | 0 | 0 | 0
68 |  | Integration Costs |  | 1.69 | 1.6466 | 1.6466
69 | Total Variable O&M costs |  | $/mwh | 1.69 | 1.6466 | 1.6466
70
71 | PPA
72
73 | Energy Price
74 |  | Base Energy Price | $/mwh |  |  |  | 185 | 39.1 | 34.75 | 34.75 | 65.3026
75 |  | Transmission Upgrades/ | $/mwh |  |  |  | 0 | included | 7.0047 | 7.0047 | 17.9067
76 |  | Interconnection | $/mwh |  |  |  |  | included | included | included | included
77 |  | PPA Administration | $/mwh |  |  |  |  | 1.3977 | 1.0377 | 1.0377 | 1.7907
78 |  | Integration Costs | $/mwh |  |  |  | 0 | 1.8176 | 4.1 | 4.1 | 0
79 | Total Energy Price |  | $/mwh |  |  |  | 185 | 42.3153 | 46.8924 | 46.8924 | 85
80
81 | Reference Year Dollars | [5 empty] | 2017 | 2020 | 2019 | 2019 | 2021
82
83 | Annual Escalation |  | % |  |  |  | none | 0% | 0% | 0% | 0%
84
85 |  |  |  | * see page 5
86 |  |  |  | Data on this table represents planning assumptions as of 11/09/16.
87 |  |  |  | represents a sensitivity will be performed

## Tax Credits
Renewable Resource Tax Credits
| Resource | Federal | Federal
Line |  | ITC | PTC
1 | Solar Inservice < 2020 | 30%
2 | Solar Inservice 2020 | 26%
3 | Solar Inservice 2021 | 22%
4 | Solar Inservice > 2021 | 10%
5 | Geothermal | 10%
6 | Wind Construction 2017 |  | 1.93 cents
7 | Wind Construction 2018 |  | 1.49 cents
8 | Wind Construction 2019 |  | 1.02 cents

## Existing 1
|  |  |  | Resource Performance Data - Existing Resources |  |  |  | Resource Performance Data - Existing Resources |  |  |  |  | Resource Performance Data - Existing Resources
|  |  |  | San Juan | San Juan | San Juan | San Juan | Four Corners | Four Corners | Palo Verde | Palo Verde | Palo Verde | Luna | Afton
|  |  |  | Unit 1 | Unit 2 | Unit 3 | Unit 4 | Unit 4 | Unit 5 | Unit 1 | Unit 2 | Unit 3
Line | [9 empty] | Owned | Owned
1 | Facility Output |  | MW | 170 | 170 | 248 | 195* | 100 | 100 | 124 | 30 | 134 | 185 | 230
2
3 | Peak Contribution |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
4
5 | Estimated Heatrate @ max output |  | Btu/kWh | 10786 | 10786 | 10475 | 10669 | 10114 | 10114 | 10300 | 10300 | 10300 | 7098 | 7029
6
7 | Expected Capacity Factor |  | % | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100%
8
9 | Forced Outage Rate |  | % | 10.5%-14.5% | 10.5%-14.5% | 10.5%-14.5% | 10.5%-14.5% | 12% | 12% | 2% | 2% | 2% | 3% | 3%
10
11 | Emission Rates
12 |  | CO2 Rate | lbs/MWh | 2150.0985 | 2102.8753 | 2165.5344 | 2173.3234 | 1929 | 2041 | 0 | 0 | 0 | 916.9442 | 902.0682
13 |  | CO Rate | lbs/MWh | 3.6456 | 4.2886 | 2.49 | 1.1983 | 0.2812 | 0.282 | 0 | 0 | 0 | 0.12741 | 0.14874
14 |  | SO2 Rate | lbs/MWh | 0.65203 | 0.54384 | 0.78915 | 0.72691 | 1.1637 | 1.7089 | 0 | 0 | 0 | 0.0046281 | 0.0045527
15 |  | NOx Rate | lbs/MWh | 2.8111 | 2.7498 | 2.7063 | 2.8091 | 4.9963 | 5.0956 | 0 | 0 | 0 | 0.10055 | 0.14547
16 |  | Hg Rate | lbs/GWh | 0.00171 | 0.0017662 | 0.0018839 | 0.0022623 | 0.0089 | 0.0079 | 0 | 0 | 0 | Do Not Monitor | Do Not Monitor
17 |  | PM10 Rate | lbs/MWh | 0.033357 | 0.033487 | 0.031475 | 0.052835 | 0.0694 | 0.1173 | 0 | 0 | 0 | 0.026798 | 0.061658
18 |  | Water Usage | gal/MWh | 647.0861 | 647.0861 | 647.0861 | 647.0861 | 496.0503 | 496.0503 | 18.1702 | 18.1702 | 18.1702 | 201.6142 | 85.4042
19
20 | Construction Time |  | months
21
22 | Expected Retirement Date |  | Year | Scenario | Year End 2017 | Year End 2017 | Scenario | Scenario | Scenario | 2046 | 2046 | 2046 | After 2036 | After 2036
23
24 | Facility Life |  | Years | Scenario | 2 | 2 | Scenario | Scenario | Scenario | 29 | 29 | 29 | 30 | 30
25
26 |  |  |  | Resource Cost & Financial Data - Existing Resources |  |  |  | Resource Cost & Financial Data - Existing Resources |  |  |  |  | Resource Cost & Financial Data - Existing Resources
27 |  |  |  | San Juan | San Juan | San Juan | San Juan | Four Corners | Four Corners | Palo Verde | Palo Verde | Palo Verde | Luna | Afton
28 |  |  |  | Unit 1 | Unit 2 | Unit 3 | Unit 4 | Unit 4 | Unit 5 | Unit 1 | Unit 2 | Unit 3
29
30 | Facility Output |  | MW | 170 | 170 | 248 | 195* | 100 | 100 | 134 | 134 | 134 | 185 | 230
31
32
33 | Utility Owned
34
35 | Preliminary Rev Requirements - Cap. Exp. (NPV) |  | k$ | 95232.7152 | 0 | 0 | 101013.102 | 193266.521 | 193266.521 | 79119.0056 | 137160.6857 | 85020.4732 | 41252.2874 | 33415.7175
36
37 | Cost of Capital |  | % | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71%
38
39 | Reference Year Dollars |  | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017
40
41 | Fixed O&M |  | $/kWyr
42 |  | Base O&M - 5 yr ave |  | 95.9876 | 58.8529 | 67.5463 | 127.8527 | 53.5825 | 53.5825 | 151.2025 | 168.6983 | 174.2971 | 21.5753 | 27.4708
43 |  | Transmission |  | 0 | 0 | 0 | 0 | 0 | 0 | 39.57 | 39.57 | 40.2027
44 |  | Fuel Handling/Gas Reservation |  | 10.8143 | 10.8143 | 10.8143 | 10.8143 | [5 empty] | 26 | 18.1
45 |  | Property Taxes |  | 6.3951 | 6.3951 | 6.3951 | 6.3951 | 5.3103 | 5.3103 | 13.7892 | 13.7892 | 12.5557 | 2.117 | 8.2177
46 |  | Total |  | 113.197 | 76.0624 | 84.7558 | 145.0622 | 58.8929 | 58.8929 | 204.5616 | 222.0574 | 227.0555 | 49.6923 | 53.7885
47
48 | Variable O&M
49 |  | Base O&M |  | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included in FOM
50 |  | Integration Costs
51 | Total Variable O&M costs |  | $/mwh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52
53 | PPA
54
55 | Energy Price
56 |  | Base Energy Price | $/mwh
57 |  | Transmission Upgrades | $/mwh
58 |  | Interconnection | $/mwh
59 |  | PPA Administration | $/mwh
60 |  | Integration Costs | $/mwh
61 | Total Energy Price |  | $/mwh
62
63 | Reference Year Dollars
64
65 | Annual Escalation |  | %
66
67 |  |  |  | * Facility output will increase to 327 MW beginning in 2018 |  |  |  | * Facility output will increase to 327 MW beginning in 2018
68 |  |  |  | Data on this table represents planning assumptions as of 11/09/16. |  |  |  | Data on this table represents planning assumptions as of 11/09/16.
69 |  |  |  | represents a sensitivity will be performed |  |  |  | represents a sensitivity will be performed

## Existing 2
| Resource Performance Data - Existing Resources |  |  | Resource Performance Data - Existing Resources |  |  |  | Resource Performance Data - Existing Resources
|  |  |  | San Juan | San Juan | San Juan | San Juan | Four Corners | Four Corners | Palo Verde | Palo Verde | Palo Verde | Luna | Afton
|  |  |  | Unit 1 | Unit 2 | Unit 3 | Unit 4 | Unit 4 | Unit 5 | Unit 1 | Unit 2 | Unit 3
Line | [9 empty] | Owned | Owned
1 | Facility Output |  | MW | 170 | 170 | 248 | 195* | 100 | 100 | 124 | 30 | 134 | 185 | 230
2
3 | Peak Contribution |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
4
5 | Estimated Heatrate @ max output |  | Btu/kWh | 10786 | 10786 | 10475 | 10669 | 10114 | 10114 | 10300 | 10300 | 10300 | 7098 | 7029
6
7 | Expected Capacity Factor |  | % | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100%
8
9 | Forced Outage Rate |  | % | 10.5%-14.5% | 10.5%-14.5% | 10.5%-14.5% | 10.5%-14.5% | 12% | 12% | 2% | 2% | 2% | 3% | 3%
10
11 | Emission Rates
12 |  | CO2 Rate | lbs/MWh | 2150.0985 | 2102.8753 | 2165.5344 | 2173.3234 | 1929 | 2041 | 0 | 0 | 0 | 916.9442 | 902.0682
13 |  | CO Rate | lbs/MWh | 3.6456 | 4.2886 | 2.49 | 1.1983 | 0.2812 | 0.282 | 0 | 0 | 0 | 0.12741 | 0.14874
14 |  | SO2 Rate | lbs/MWh | 0.65203 | 0.54384 | 0.78915 | 0.72691 | 1.1637 | 1.7089 | 0 | 0 | 0 | 0.0046281 | 0.0045527
15 |  | NOx Rate | lbs/MWh | 2.8111 | 2.7498 | 2.7063 | 2.8091 | 4.9963 | 5.0956 | 0 | 0 | 0 | 0.10055 | 0.14547
16 |  | Hg Rate | lbs/GWh | 0.00171 | 0.0017662 | 0.0018839 | 0.0022623 | 0.0089 | 0.0079 | 0 | 0 | 0 | Do Not Monitor | Do Not Monitor
17 |  | PM10 Rate | lbs/MWh | 0.033357 | 0.033487 | 0.031475 | 0.052835 | 0.0694 | 0.1173 | 0 | 0 | 0 | 0.026798 | 0.061658
18 |  | Water Usage | gal/MWh | 647.0861 | 647.0861 | 647.0861 | 647.0861 | 496.0503 | 496.0503 | 18.1702 | 18.1702 | 18.1702 | 201.6142 | 85.4042
19
20 | Construction Time |  | months
21
22 | Expected Retirement Date |  | Year | Scenario | Year End 2017 | Year End 2017 | Scenario | Scenario | Scenario | 2046 | 2046 | 2046 | After 2036 | After 2036
23
24 | Facility Life |  | Years | Scenario | 2 | 2 | Scenario | Scenario | Scenario | 29 | 29 | 29 | 30 | 30
25
26 | Resource Cost & Financial Data - Existing Resources |  |  | Resource Cost & Financial Data - Existing Resources |  |  |  | Resource Cost & Financial Data - Existing Resources
27 |  |  |  | San Juan | San Juan | San Juan | San Juan | Four Corners | Four Corners | Palo Verde | Palo Verde | Palo Verde | Luna | Afton
28 |  |  |  | Unit 1 | Unit 2 | Unit 3 | Unit 4 | Unit 4 | Unit 5 | Unit 1 | Unit 2 | Unit 3
29
30 | Facility Output |  | MW | 170 | 170 | 248 | 195* | 100 | 100 | 134 | 134 | 134 | 185 | 230
31
32
33 | Utility Owned
34
35 | Preliminary Rev Requirements - Cap. Exp. (NPV) |  | k$ | 95232.7152 | 0 | 0 | 101013.102 | 193266.521 | 193266.521 | 79119.0056 | 137160.6857 | 85020.4732 | 41252.2874 | 33415.7175
36
37 | Cost of Capital |  | % | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71%
38
39 | Reference Year Dollars |  | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017
40
41 | Fixed O&M |  | $/kWyr
42 |  | Base O&M - 5 yr ave |  | 95.9876 | 58.8529 | 67.5463 | 127.8527 | 53.5825 | 53.5825 | 151.2025 | 168.6983 | 174.2971 | 21.5753 | 27.4708
43 |  | Transmission |  | 0 | 0 | 0 | 0 | 0 | 0 | 39.57 | 39.57 | 40.2027
44 |  | Fuel Handling/Gas Reservation |  | 10.8143 | 10.8143 | 10.8143 | 10.8143 | [5 empty] | 26 | 18.1
45 |  | Property Taxes |  | 6.3951 | 6.3951 | 6.3951 | 6.3951 | 5.3103 | 5.3103 | 13.7892 | 13.7892 | 12.5557 | 2.117 | 8.2177
46 |  | Total |  | 113.197 | 76.0624 | 84.7558 | 145.0622 | 58.8929 | 58.8929 | 204.5616 | 222.0574 | 227.0555 | 49.6923 | 53.7885
47
48 | Variable O&M
49 |  | Base O&M |  | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included in FOM
50 |  | Integration Costs
51 | Total Variable O&M costs |  | $/mwh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52
53 | PPA
54
55 | Energy Price
56 |  | Base Energy Price | $/mwh
57 |  | Transmission Upgrades | $/mwh
58 |  | Interconnection | $/mwh
59 |  | PPA Administration | $/mwh
60 |  | Integration Costs | $/mwh
61 | Total Energy Price |  | $/mwh
62
63 | Reference Year Dollars
64
65 | Annual Escalation |  | %
66
67 | * Facility output will increase to 327 MW beginning in 2018
68 | Data on this table represents planning assumptions as of 11/09/16.
69 | represents a sensitivity will be performed

## Existing 3
|  |  |  | Resource Performance Data - Existing Resources | [6 empty] | Resource Performance Data - Existing Resources
|  |  |  | Lordsburg | Lordsburg | La Luz | Reeves | Reeves | Reeves | Rio Bravo | Solar | Solar | Valencia | NM Wind | Red Mesa | Dale Burgett
|  |  |  | Unit 1 | Unit 2 |  | Unit 1 | Unit 2 | Unit 3 |  | Fixed Tilt | Tracking |  | Energy Center | Wind
Line
1 | Facility Output |  | MW | 40 | 40 | 40 | 44 | 44 | 66 | 138 | 40 | 67 | 145 | 200 | 102 | 8
2
3 | Peak Contribution/Estimated ELCC |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 55% | 71% | 100% | 5% | 5% | 56%
4
5
6
7
8 | Estimated Heatrate @ max output |  | Btu/kWh | 9596 | 9576 | 9485 | 12039.2857 | 12039.2857 | 12039.2857 | 10284 |  |  | 10177
9
10 | Expected Capacity Factor |  | % | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-100% | 0-28% | 0-33% | 0-100% | 0-100% | 0-100% | 0-100%
11
12 | Forced Outage Rate |  | % | 3% | 3% | 3% | 3% | 3% | 3% | 3% |  |  | 3%
13
14 | Emission Rates
15 |  | CO2 Rate | lbs/MWh | 1368.5001 | 1304.159 | 1160 | 1461.4415 | 1434.5648 | 1401.4521 | 1398.2604 | 0 | 0 | 1338.8007 | 0 | 0 | 0
16 |  | CO Rate | lbs/MWh | 0.72499 | 0.49825 | 0.08918 | 0.039343 | 0.014611 | 0.7946 | 0.015121 | 0 | 0 | 0.14434 | 0 | 0 | 0
17 |  | SO2 Rate | lbs/MWh | 0.0068618 | 0.0065141 | 0.13132 | 0.0073824 | 0.0072532 | 0.0070645 | 0.007788 | 0 | 0 | 0.0067517 | 0 | 0 | 0
18 |  | NOx Rate | lbs/MWh | 1.2008 | 1.1859 | 0.0098 | 2.8424 | 3.1048 | 2.7745 | 0.50314 | 0 | 0 | 0.3889 | 0 | 0 | 0
19 |  | Hg Rage | lbs/MWh | Do Not Monitor | Do Not Monitor | Do Not Monitor | Do Not Monitor | Do Not Monitor | Do Not Monitor | Do Not Monitor | 0 | 0 | Do Not Monitor | 0 | 0 | 0
20 |  | PM10 Rate | lbs/MWh | 0.1411 | 0.13379 | 0.083779 | 0.090843 | 0.089178 | 0.087098 | 0.026 | 0 | 0 | 0.18671 | 0 | 0 | 0
21 |  | Water Usage | gal/MWh | 100 | 100 | 100 | 619.2232 | 619.2232 | 619.2232 | 9.8975 | 0 | 0 | 10.2389 | 0 | 0 | 0
22
23 | Construction Time |  | months
24
25 | Expected Retirement Date |  | Year | After 2036 | After 2036 | After 2036 | After 2036 | After 2036 | After 2036 | After 2036 | After 2036 | After 2036
26
27 | Contract Expiration |  | Year | [9 empty] | May 2028 | July 2028 | Dec 2035 | Jan 2034
28
29 | Facility Life |  | Years | 40 | 40 | 40 | Sensitivity | Sensitivity | Sensitivity | 40 | 25 | 25
30
31
32 |  |  |  | Resource Cost & Financial Data - Existing Resources | [6 empty] | Resource Cost & Financial Data - Existing Resources
33 |  |  |  | Lordsburg | Lordsburg | La Luz | Reeves | Reeves | Reeves | Rio Bravo | Solar | Solar | Valencia | NM Wind | Red Mesa | Dale Burgett
34 |  |  |  | Unit 1 | Unit 2 |  | Unit 1 | Unit 2 | Unit 3 |  |  |  |  | Energy Center | Wind
35
36 | Facility Output |  | MW | 40 | 40 | 40 | 44 | 44 | 66 | 138 | 40 | 67 | 145 | 200 | 102 | 8
37
38
39 | Utility Owned
40
41 | Preliminary Rev Requirements - Cap. Exp. (NPV) |  | k$ | 874.4767 | 874.4767 | 2754.426 | 3306.1768 | 3306.1768 | 4959.2651 | 2053.5897
42
43 | Cost of Capital |  | % | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71% | 7.71%
44
45 | Reference Year Dollars |  | 2016 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017
46
47 | 5 Yr Fixed O&M |  | $/kWyr
48 |  | Base O&M |  | 14.6409 | 14.6409 | 24.2437 | 28.2359 | 28.2359 | 28.2359 | 14.9204 | 23.4518 | 23.4518 | 0 | 0 | 0 | 0
49 |  | Transmission | [10 empty] | 0 | 0 | 0 | 0
50 |  | Gas Reservation |  | 24.3 | 24.3 | 24.3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
51 |  | Property Taxes |  | 3.9626 | 3.9626 | 11.4242 | 3.9189 | 3.9189 | 3.9189 | 2.7989 | 23.1335 | 23.1335 | 0 | 0 | 0 | 0
52 |  | Total |  | 42.9035 | 42.9035 | 59.9679 | 32.1548 | 32.1548 | 32.1548 | 17.7193 | 46.5853 | 46.5853 | 0 | 0 | 0 | 0
53
54 | Variable O&M
55 |  | Base O&M |  | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | included FOM | 0 | 0 | 0 | 0
56 |  | Integration Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | Total Variable O&M costs |  | $/mwh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58
59 | PPA
60
61 | Demand |  | $/kWmo | [9 empty] | 8.15
62 | Fixed O&M |  | $/kWmo | [9 empty] | 1.79
63 | Gas Reservation Fee |  | $/kWmo | [9 empty] | 12.4
64 |  | Total | [10 empty] | 22.34 | 0 | 0 | 0
65
66 | Variable/Energy Price (non fuel)
67 |  | Base Energy Price | [10 empty] | 0 | 27.25 | 68.25 | 104.02
68 |  | Transmission Service | [10 empty] | 0 | 0 | 0 | 0
69 |  | Variable O&M | [10 empty] | 6.72 | 0 | 0 | 0
70 |  | Integration Costs | [10 empty] | 0 | 0 | 0 | 0
71 | Total Energy Price |  | $/mwh | [9 empty] | 6.72 | 27.25 | 68.25 | 104.02
72
73 | Reference Year Dollars | [11 empty] | 2017 | 2017 | 2017 | 2017
74
75 | Annual Escalation |  | % | [10 empty] | Fixed | 2% | 2.75%
76
77 |  |  |  | Data on this table represents planning assumptions as of 11/09/16. | [5 empty] | Data on this table represents planning assumptions as of 11/09/16.
78 |  |  |  | represents a sensitivity will be performed | [5 empty] | represents a sensitivity will be performed