## Slide 1: December 19 2024 PRAC Meeting
Generation production Allocation

## Slide 2: Presentation FINDINGS
Review Expected Unserved Energy (“EUE”)
Risk hours projected for 2028 include summer evenings and winter mornings
75% EUE is 40 hours in 2028
Two segments: a) 8760 non-Area Control Error (“ACE”) hours and b) 75% EUE Area Control Error hours), provide a reasonable alignment of costs to class use. These two segments align the cost allocation of resources used in risk hours with the loads that are served during that time

## Slide 3: Review EUE and reliability target
PNM plans the system per industry standards approved by the NMPRC.
NMPRC has approved a reliability target of 1 day in 10 years. This is the Loss of Load Expectation (“LOLE”) target used for resource planning.
EUE tells you the total amount of modeled energy that would be lost during the one day in a 10- year outage. EUE is expressed as total kWh/MWh at risk.
Increasing system reliability requires increasing portfolio costs. 1 day in 10 years is a reasonable target that is common for electric utilities.

## Slide 4: 2028 risk includes evenings and winter mornings
EUE is high pre-dawn in January and February.
  Main driver is that energy is stored during the day and depleted overnight when solar resources are idle.
EUE is high in the Summer around sunset.
  Main driver is that decreasing renewable production is not sufficient to meet evening loads.

## Slide 5: 2028 EUE Heat Map
% of EUE Capacity |  | Month |  |  |  |  |  |  |  |  |  |  | 
 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Hour of Day | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 2 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 3 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 4 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 5 | 0% | 4% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 6 | 1% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 7 | 4% | 18% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 8 | 2% | 5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1%
 | 9 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 11 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 12 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 17 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 0% | 0% | 0%
 | 18 | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 1% | 0% | 0% | 0% | 0%
 | 19 | 0% | 0% | 0% | 0% | 0% | 0% | 3% | 2% | 2% | 0% | 0% | 0%
 | 20 | 0% | 0% | 0% | 0% | 0% | 2% | 16% | 6% | 3% | 0% | 0% | 0%
 | 21 | 0% | 0% | 0% | 0% | 0% | 0% | 7% | 2% | 1% | 0% | 0% | 0%
 | 22 | 0% | 0% | 0% | 0% | 0% | 0% | 2% | 0% | 1% | 0% | 0% | 0%
 | 23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
 | 24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%

## Slide 6: Production Capacity Planning
75% EUE is appropriate to select risk hours that drive production additions and to capture the risks of serving load reliably throughout the year.
  Capacity planning is now driven by non-solar hours.
  Solar resources are “energy only” and add little capacity
  Generation Production $ are spent for non-solar hour resources.

## Slide 7: Generation Production Risk Hours
The total EUE and number of EUE hours are an indication of the risk associated with serving load during a given period.
Based on 07-01-2025 through 06-30-2026, 75% of EUE is 87 hours.
  Total EUE is about 161 MWh.
Based on calendar 2028, 75% EUE is 40 hours.
  Total EUE is about 5.5 MWh.
The amount of total EUE and the number of EUE hours will vary each study period. However, using the top 75% of EUE hours will always capture the riskiest hours.

## Slide 8: TWO-segment Production Allocation
75% EUE ACE with 8760 Non-ACE adapts to each study and allocates the cost of ACE and non-ACE resources to each class based on their usage pattern in the study period.
3S1W could likely miss the riskiest hours almost completely as renewable penetration increases.
Different usage patterns, including both the time and amount of load, drive production costs very differently.
For example, a school that operates during the daylight hours is unlikely to drive spending on resource additions because usage at other times (when the school is closed) put more stress on the system. Very little production resource needs are caused by this customer. A customer with this type of usage would get a relatively lower portion of the ACE production costs.
A second example is a sports venue that is primarily using energy after 5pm, meaning it has the highest demands around sunset and contributes to the need to add more production capacity. A customer with this type of use would get a higher portion of the ACE production costs.
ACE resources generally result in a higher capacity cost than non-ACE resources.