## Slide 1
REQUIRED FEATURES
Site Address (must match application).
Info Box that contains the Quantity, Manufacturer, and Model Number for the Modules and Inverters.
If Energy Storage is applicable the info box must include its Quantity, Manufacturer, Model Number and Mode of operation.
All equipment labelled with callouts, not in a legend, in correct order, and disconnect between inverter and interconnection point.
Label the Quantity, Manufacturer, and Model Number for the Modules and Inverters in their callouts on the diagram.
Inverter Output Voltage.
Production Meter Socket rated amperage (i.e 100A or 200A if system greater than 10kW AC) Note: neutrals cannot be bonded
All ESS must have UL9540 listing.
All Inverters must have both UL1741 SB and IEE1547-2018 listings.
Helpful Features
Voltage at point of Interconnection must match inverter output.
If including a Generator or EV charger an NSD application must be submitted.
Components and connections shown are for illustrative purposes only
1. This illustrative sketch is not intended to specify utility interconnection or safety requirements.
2. PNM may request additional information if determined it is needed during the screening process.
3. This illustrative sketch is not intended to provide electrical design or code compliance directives.
4. Some components and connections shown may be internal to the inverter. The manufacturer and model number of the inverter must be shown on the drawing.
5. All switches, fuses, and mechanical interlock mechanisms which are part of the operating scheme to isolate the customers generating equipment from the utility during emergency
or maintenance conditions must be shown on the single-line diagram.
6. The narrative description accompanying the single line interconnection diagram must contain sufficient detail to determine if the components in, and the operation of, the
interconnection and protection systems meet the utility’s interconnection and safety standards.
One Line Diagram:
Back-Fed Breaker
Info Box
Module(s): Quantity, Manufacturer, Model Number Inverter(s): Quantity, Manufacturer, Model Number *Calculations not required.
(If Applicable) Storage: Quantity, Manufacturer, Model Number CEC Certified Mode of Operation: i.e., Backup
505 Camino de Solar Albuquerque, NM 87111
Note: PNM may request additional information if
determined it is needed during the screening process

## Slide 2
REQUIRED FEATURES
Site Address (must match application).
Info Box that contains the Quantity, Manufacturer, and Model Number for the Modules and Inverters.
If Energy Storage is applicable the info box must include its Quantity, Manufacturer, Model Number and Mode of operation.
All equipment labelled with callouts, not in a legend, in correct order, and disconnect between inverter and interconnection point.
Label the Quantity, Manufacturer, and Model Number for the Modules and Inverters in their callouts on the diagram.
Inverter Output Voltage.
All ESS must have UL9540 listing.
All Inverters must have both UL1741 SB and IEE1547-2018.
Production Meter is optional for systems sized 10 kW and under.
Helpful Features
Voltage at point of Interconnection must match inverter output.
If including a Generator or EV charger an NSD application must be submitted.
Components and connections shown are for illustrative purposes only
1. This illustrative sketch is not intended to specify utility interconnection or safety requirements.
2. PNM may request additional information if determined it is needed during the screening process.
3. This illustrative sketch is not intended to provide electrical design or code compliance directives.
4. Some components and connections shown may be internal to the inverter. The manufacturer and model number of the inverter must be shown on the drawing.
5. All switches, fuses, and mechanical interlock mechanisms which are part of the operating scheme to isolate the customers generating equipment from the utility during emergency
or maintenance conditions must be shown on the single-line diagram.
6. The narrative description accompanying the single line interconnection diagram must contain sufficient detail to determine if the components in, and the operation of, the
interconnection and protection systems meet the utility’s interconnection and safety standards.
One Line Diagram:
Back-Fed Breaker
For systems at or under 10kW AC
Info Box
Module(s): Quantity, Manufacturer, Model Number Inverter(s): Quantity, Manufacturer, Model Number *Calculations not required.
(If Applicable) Storage: Quantity, Manufacturer, Model Number CEC Certified Mode of Operation: i.e., Backup
505 Camino de Solar Albuquerque, NM 87111
Note: PNM may request additional information if
determined it is needed during the screening process

## Slide 3
REQUIRED FEATURES
Site Address (must match application).
Info Box that contains the Quantity, Manufacturer, and Model Number for the Modules and Inverters.
All equipment labelled with callouts, not in a legend, in correct order, and disconnect between inverter and interconnection point.
Label the Quantity, Manufacturer, and Model Number for the Modules and Inverters in their callouts on the diagram.
Inverter Output Voltage.
Production Meter Socket rated amperage (i.e 100A or 200A if system greater than 10kW AC). Must be Fused and Service Entrance Rated. Note: Neutrals cannot be bonded.
All Inverters must have both UL1741 SB and IEE1547-2018.
Line side taps are not allowed with ESS systems.
Production Meter is optional for systems sized 10 kW.
Helpful Features
Voltage at point of Interconnection must match inverter output
If including a Generator or EV charger an NSD application must be submitted
Components and connections shown are for illustrative purposes only
1. This illustrative sketch is not intended to specify utility interconnection or safety requirements.
2. PNM may request additional information if determined it is needed during the screening process.
3. This illustrative sketch is not intended to provide electrical design or code compliance directives.
4. Some components and connections shown may be internal to the inverter. The manufacturer and model number of the inverter must be shown on the drawing.
5. All switches, fuses, and mechanical interlock mechanisms which are part of the operating scheme to isolate the customers generating equipment from the utility during emergency
or maintenance conditions must be shown on the single-line diagram.
6. The narrative description accompanying the single line interconnection diagram must contain sufficient detail to determine if the components in, and the operation of, the
interconnection and protection systems meet the utility’s interconnection and safety standards.
One Line Diagram:
Line Side Tap
505 Camino de Solar Albuquerque, NM 87111
Info Box
Module(s): Quantity, Manufacturer, Model Number Inverter(s): Quantity, Manufacturer, Model Number *Calculations not required. *Line side taps not allowed with ESS systems
Note: PNM may request additional information if
determined it is needed during the screening process

## Slide 4
One Line Diagram:
Expansion
Info Box
Existing (E) Module(s): Quantity, Manufacturer, Model Number Inverter(s): Quantity, Manufacturer, Model Number New (N) Module(s) Quantity, Manufacturer, Model Number Inverter(s): Quantity, Manufacturer, Model Number *Calculations not required. *Line side taps not allowed with ESS systems
(If Applicable) Storage (E) or (N): Quantity, Manufacturer, Model Number Mode of Operation: i.e., Backup
REQUIRED FEATURES
Site Address (must match application).
Info Box that contains the Quantity, Manufacturer, and Model Number for the Modules and Inverters.
If Energy Storage is applicable the info box must include its Quantity, Manufacturer, Model Number and Mode of operation.
All equipment labelled with callouts, not in a legend, in correct order, and PV disconnect between inverter and interconnection point.
Label the Quantity, Manufacturer, and Model Number for all Modules and Inverters including previously installed.
For an Expansion, please clearly label the equipment as New or Existing. Please also make this distinction in the Info box.
If V2G functionality is desired, EV charger must be depicted in diagrams and application.
Inverter Output Voltage.
Production Meter Socket rated amperage (i.e100A or 200A if system greater than 10kW AC) Note: neutrals cannot be bonded.
All ESS must have UL9540 listing.
All new Inverters (submitted on or after March 29, 2024) must have both UL1741 SB and IEE1547-2018.
Helpful Features
Voltage at point of Interconnection must match inverter output.
If including a Generator or EV charger an NSD application must be submitted.
505 Camino de Solar Albuquerque, NM 87111
Note: PNM may request additional information if
determined it is needed during the screening process

## Slide 5: Additional Information
• For 3-phase systems Three Line Diagram is required.
• A Three-line diagram may be requested by reviewers as deemed necessary.
• For Large (>10 kW AC) and/or 3-phase systems:
• Include references to PNM Meter Standard
• Production meter Socket must be rated at least 200A
For Systems >50 kW AC
    Utilize a fused disconnect. For larger systems, pressure bolted disconnects are recommended
    1-line diagram, 3-line diagram, and Site Map must be PE Stamped
• For Battery Backup or Energy Storage Systems, please refer to PNM Interconnection ----- and Safety Standards.
    All diagrams are evaluated to ensure compliance with PNM metering and Interconnection and Safety Standards. This evaluation does not imply NEC compliance.
• For technical requirements for Interconnecting Distributed Energy Resources (DER) to ----PNM’s electric distribution system please see PNM’s Technical Interconnection and --------Interoperability Requirements (TIIR).
    PNM Technical Interconnection and Interoperability Requirements